## Taul2
Title | Info | ID | Unit | Size | Factor | Min | Max | Default | Mode
BT1 Outdoor temp | Outdoor temperature | 40004 | °C | s16 | 10 | 0 | 0 | 0 | R
EB23-BT2 Supply temp S4 | Supply temperature for system 4 | 40005 | °C | s16 | 10 | 0 | 0 | 0 | R
EB22-BT2 Supply temp S3 | Supply temperature for system 3 | 40006 | °C | s16 | 10 | 0 | 0 | 0 | R
EB21-BT2 Supply temp S2 | Supply temperature for system 2 | 40007 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP15-BT3 Return temp |  | 40011 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP14-BT3 Return temp | Return temperature | 40012 | °C | s16 | 10 | 0 | 0 | 0 | R
BT7 Hot Water top |  | 40013 | °C | s16 | 10 | 0 | 0 | 0 | R
BT6 Hot Water load |  | 40014 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP14-BT10 Brine in temp |  | 40015 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP14-BT11 Brine out temp |  | 40016 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP14-BT12 Cond. out |  | 40017 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP14-BT14 Hot gas temp |  | 40018 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP14-BT15 Liquid line |  | 40019 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP14-BT17 Suction |  | 40022 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-BT20 Exhaust air temp. |  | 40025 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-BT21 Vented air temp. |  | 40026 | °C | s16 | 10 | 0 | 0 | 0 | R
AZ1-BT26 Temp Collector in FLM 1 | Connected to the FLM module | 40028 | °C | s16 | 10 | 0 | 0 | 0 | R
AZ1-BT27 Temp Collector out FLM 1 | Connected to the FLM module | 40029 | °C | s16 | 10 | 0 | 0 | 0 | R
EB23-BT50 Room Temp S4 |  | 40030 | °C | s16 | 10 | 0 | 0 | 0 | R
EB22-BT50 Room Temp S3 |  | 40031 | °C | s16 | 10 | 0 | 0 | 0 | R
EB21-BT50 Room Temp S2 |  | 40032 | °C | s16 | 10 | 0 | 0 | 0 | R
BT50 Room Temp S1 |  | 40033 | °C | s16 | 10 | 0 | 0 | 0 | R
CL11-BT51 Pool 1 Temp |  | 40042 | °C | s16 | 10 | 0 | 0 | 0 | R
EP8-BT53 Solar Panel Temp |  | 40043 | °C | s16 | 10 | 0 | 0 | 0 | R
EP8-BT54 Solar Load Temp |  | 40044 | °C | s16 | 10 | 0 | 0 | 0 | R
EQ1-BT64 PCS4 Supply Temp | PCS4 Only | 40045 | °C | s16 | 10 | 0 | 0 | 0 | R
EQ1-BT65 PCS4 Return Temp | PCS4 Only | 40046 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-FD1 Temperature limiter |  | 40054 |  | s16 | 1 | 0 | 0 | 0 | R
BT1 Average | EB100-BT1 Outdoor temperature average | 40067 | °C | s16 | 10 | 0 | 0 | 0 | R
EM1-BT52 Boiler temperature | Temperature of Boiler | 40070 | °C | s16 | 10 | 0 | 0 | 0 | R
BT25 external supply temp |  | 40071 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-FR1 Anode Status |  | 40074 |  | s16 | 1 | 0 | 0 | 0 | R
EB100-BE3 Current Phase 3 |  | 40079 | A | s32 | 10 | 0 | 0 | 0 | R
EB100-BE2 Current Phase 2 |  | 40081 | A | s32 | 10 | 0 | 0 | 0 | R
EB100-BE1 Current Phase 1 |  | 40083 | A | s32 | 10 | 0 | 0 | 0 | R
EB100-EP15-BT11 Brine out temp |  | 40085 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP15-BT12 Cond. out |  | 40086 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP15-BT14 Hot gas temp |  | 40087 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP15-BT15 Liquid line |  | 40088 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP15-BT17 Suction |  | 40089 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP15-BT10 Brine in temp |  | 40100 | °C | s16 | 10 | 0 | 0 | 0 | R
CL11-BT51 Pool 2 Temp |  | 40106 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-BT20 Exhaust air temp. |  | 40107 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-BT20 Exhaust air temp. |  | 40108 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-BT20 Exhaust air temp. |  | 40109 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-BT21 Vented air temp. |  | 40110 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-BT21 Vented air temp. |  | 40111 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-BT21 Vented air temp. |  | 40112 | °C | s16 | 10 | 0 | 0 | 0 | R
AZ1-BT26 Temp Collector in FLM 4 | Connected to the FLM module | 40113 | °C | s16 | 10 | 0 | 0 | 0 | R
AZ1-BT26 Temp Collector in FLM 3 | Connected to the FLM module | 40114 | °C | s16 | 10 | 0 | 0 | 0 | R
AZ1-BT26 Temp Collector in FLM 2 | Connected to the FLM module | 40115 | °C | s16 | 10 | 0 | 0 | 0 | R
AZ1-BT27 Temp Collector out FLM 4 | Connected to the FLM module | 40116 | °C | s16 | 10 | 0 | 0 | 0 | R
AZ1-BT27 Temp Collector out FLM 3 | Connected to the FLM module | 40117 | °C | s16 | 10 | 0 | 0 | 0 | R
AZ1-BT27 Temp Collector out FLM 2 | Connected to the FLM module | 40118 | °C | s16 | 10 | 0 | 0 | 0 | R
EB23-BT3 Return temp S4 | Return temperature for system 4 | 40127 | °C | s16 | 10 | 0 | 0 | 0 | R
EB22-BT3 Return temp S3 | Return temperature for system 3 | 40128 | °C | s16 | 10 | 0 | 0 | 0 | R
EB21-BT3 Return temp S2 | Return temperature for system 2 | 40129 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP15-BP8 Pressure Transmitter | Temperture reported by the pressure transmitter | 40131 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP14-BP8 Pressure Transmitter | Temperture reported by the pressure transmitter | 40132 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP15-BT29 | Compressor oil temperature | 40145 | °C | s16 | 10 | 0 | 0 | 0 | R
EB100-EP14-BT29 | Compressor oil temperature | 40146 | °C | s16 | 10 | 0 | 0 | 0 | R
BT70 HW supply temp. | Hot water supply temperature | 40147 | °C | s16 | 10 | 0 | 0 | 0 | R
BT71 Ext. Return temp |  | 40152 | °C | s16 | 10 | 0 | 0 | 0 | R
EQ1-BT57 Collector temp. | External collector temperature for ACS | 40155 | °C | s16 | 10 | 0 | 0 | 0 | R
EQ1-BT75 Heatdump temp. | Heating medium dump temperature for ACS | 40156 | °C | s16 | 10 | 0 | 0 | 0 | R
Software version |  | 43001 |  | u16 | 1 | 0 | 0 | 0 | R
Degree Minutes |  | 43005 |  | s16 | 10 | -30000 | 30000 | 0 | R/W
Calculated Supply Temperature S4 |  | 43006 | °C | s16 | 10 | 0 | 0 | 0 | R
Calculated Supply Temperature S3 |  | 43007 | °C | s16 | 10 | 0 | 0 | 0 | R
Calculated Supply Temperature S2 |  | 43008 | °C | s16 | 10 | 0 | 0 | 0 | R
Calculated Supply Temperature S1 |  | 43009 | °C | s16 | 10 | 0 | 0 | 0 | R
Freeze Protection Status | 1 = Freeze protection active | 43013 |  | u8 | 1 | 0 | 0 | 0 | R
Tot. op.time add. | Total electric additive operation time | 43081 | h | s32 | 10 | 0 | 9999999 | 0 | R
Int. el.add. Power | Current power from the internal electrical addition | 43084 | kW | s16 | 100 | 0 | 0 | 0 | R
Prio | Indicates what heating action (HW/heat/pool) currently prioritised 10=Off 20=Hot Water 30=Heat 40=Pool 41=Pool 2 50=Transfer 60=Cooling | 43086 |  | u8 | 1 | 0 | 0 | 0 | R
Int. el.add. State | State of the internal electrical addition | 43091 |  | u8 | 1 | 0 | 0 | 0 | R
HPAC state | State of the HPAC cooling accessory. | 43103 |  | u8 | 1 | 0 | 0 | 0 | R
Fan speed current | The current fan speed after scheduling and blocks are considered | 43108 | % | u8 | 1 | 0 | 0 | 0 | R
Tot. HW op.time add. | Total electric additive operation time in hot water mode | 43239 | h | s32 | 10 | 0 | 9999999 | 0 | R
Compressor starts EB100-EP15 | Number of compressorer starts | 43414 |  | s32 | 1 | 0 | 0 | 0 | R
Compressor starts EB100-EP14 | Number of compressorer starts | 43416 |  | s32 | 1 | 0 | 9999999 | 0 | R
Tot. op.time compr. EB100-EP15 | Total compressorer operation time | 43418 | h | s32 | 1 | 0 | 0 | 0 | R
Tot. op.time compr. EB100-EP14 | Total compressorer operation time | 43420 | h | s32 | 1 | 0 | 9999999 | 0 | R
Tot. HW op.time compr. EB100-EP15 | Total compressorer operation time in hot water mode | 43422 | h | s32 | 1 | 0 | 0 | 0 | R
Tot. HW op.time compr. EB100-EP14 | Total compressorer operation time in hot water mode | 43424 | h | s32 | 1 | 0 | 9999999 | 0 | R
Compressor State EP15 | 20 = Stopped, 40 = Starting, 60 = Running, 100 = Stopping | 43426 |  | u8 | 1 | 0 | 0 | 0 | R
Compressor State EP14 | 20 = Stopped, 40 = Starting, 60 = Running, 100 = Stopping | 43427 |  | u8 | 1 | 0 | 0 | 0 | R
Compressor status EP15 | Indicates if the compressor is supplied with power 0=Off 1=On | 43434 |  | u8 | 1 | 0 | 0 | 0 | R
Compressor status EP14 | Indicates if the compressor is supplied with power 0=Off 1=On | 43435 |  | u8 | 1 | 0 | 0 | 0 | R
HM-pump Status EP15 | Status of the circ. pump | 43436 |  | u8 | 1 | 0 | 0 | 0 | R
HM-pump Status EP14 | Status of the circ. pump | 43437 |  | u8 | 1 | 0 | 0 | 0 | R
Brinepump Status EP15 | Status of the Brine pump | 43438 |  | u8 | 1 | 0 | 0 | 0 | R
Brinepump Status EP14 | Status of the Brine pump | 43439 |  | u8 | 1 | 0 | 0 | 0 | R
PCA-Base Relays EP15 | Indicates the active relays on the PCA-Base card. The information is binary encoded | 43513 |  | u8 | 1 | 0 | 0 | 0 | R
PCA-Base Relays EP14 | Indicates the active relays on the PCA-Base card. The information is binary encoded | 43514 |  | u8 | 1 | 0 | 0 | 0 | R
PCA-Power Relays EP14 | Indicates the active relays on the PCA-Power card. The information is binary encoded | 43516 |  | u8 | 1 | 0 | 0 | 0 | R
EB108-EP15-BT3 Return temp. | Return temperature | 43600 | °C | s16 | 10 | 0 | 0 | 0 | R
EB108-EP15-BT10 Brine in temp |  | 43601 | °C | s16 | 10 | 0 | 0 | 0 | R
EB108-EP15-BT11 Brine out temp |  | 43602 | °C | s16 | 10 | 0 | 0 | 0 | R
EB108-EP15-BT12 Cond. out |  | 43603 | °C | s16 | 10 | 0 | 0 | 0 | R
EB108-EP15-BT14 Hot gas temp |  | 43604 | °C | s16 | 10 | 0 | 0 | 0 | R
EB108-EP15-BT15 Liquid line |  | 43605 | °C | s16 | 10 | 0 | 0 | 0 | R
EB108-EP15-BT17 Suction |  | 43606 | °C | s16 | 10 | 0 | 0 | 0 | R
EB108-EP15-BT29 Compr. Oil. temp. |  | 43607 | °C | s16 | 10 | 0 | 0 | 0 | R
EB108-EP15-BP8 Pressure transmitter |  | 43608 | °C | s16 | 10 | 0 | 0 | 0 | R
EB108-EP15 Compressor State |  | 43609 |  | u8 | 1 | 0 | 0 | 0 | R
EB108-EP15 Compr. time to start |  | 43610 |  | u8 | 1 | 0 | 0 | 0 | R
EB108-EP15 Relay status |  | 43611 |  | u16 | 1 | 0 | 0 | 0 | R
EB108-EP15 Heat med. pump status |  | 43612 |  | u8 | 1 | 0 | 0 | 0 | R
EB108-EP15 Brine pump status |  | 43613 |  | u8 | 1 | 0 | 0 | 0 | R
EB108-EP15 Compressor starts |  | 43614 |  | u32 | 1 | 0 | 0 | 0 | R
EB108-EP15 Tot. op.time compr |  | 43616 | h | u32 | 1 | 0 | 0 | 0 | R
EB108-EP15 Tot. HW op.time compr |  | 43618 | h | u32 | 1 | 0 | 0 | 0 | R
EB108-EP15 Alarm number | The value indicates the most severe current alarm | 43620 |  | u16 | 1 | 0 | 0 | 0 | R
EB108-EP14-BT3 Return temp. | Return temperature | 43621 | °C | s16 | 10 | 0 | 0 | 0 | R
EB108-EP14-BT10 Brine in temp |  | 43622 | °C | s16 | 10 | 0 | 0 | 0 | R
EB108-EP14-BT11 Brine out temp |  | 43623 | °C | s16 | 10 | 0 | 0 | 0 | R
EB108-EP14-BT12 Cond. out |  | 43624 | °C | s16 | 10 | 0 | 0 | 0 | R
EB108-EP14-BT14 Hot gas temp |  | 43625 | °C | s16 | 10 | 0 | 0 | 0 | R
EB108-EP14-BT15 Liquid line |  | 43626 | °C | s16 | 10 | 0 | 0 | 0 | R
EB108-EP14-BT17 Suction |  | 43627 | °C | s16 | 10 | 0 | 0 | 0 | R
EB108-EP14-BT29 Compr. Oil. temp. |  | 43628 | °C | s16 | 10 | 0 | 0 | 0 | R
EB108-EP14-BP8 Pressure transmitter |  | 43629 | °C | s16 | 10 | 0 | 0 | 0 | R
EB108-EP14 Compressor State |  | 43630 |  | u8 | 1 | 0 | 0 | 0 | R
EB108-EP14 Compr. time to start |  | 43631 |  | u8 | 1 | 0 | 0 | 0 | R
EB108-EP14 Relay status |  | 43632 |  | u16 | 1 | 0 | 0 | 0 | R
EB108-EP14 Heat med. pump status |  | 43633 |  | u8 | 1 | 0 | 0 | 0 | R
EB108-EP14 Brine pump status |  | 43634 |  | u8 | 1 | 0 | 0 | 0 | R
EB108-EP14 Compressor starts |  | 43635 |  | u32 | 1 | 0 | 0 | 0 | R
EB108-EP14 Tot. op.time compr |  | 43637 | h | u32 | 1 | 0 | 0 | 0 | R
EB108-EP14 Tot. HW op.time compr |  | 43639 | h | u32 | 1 | 0 | 0 | 0 | R
EB108-EP14 Alarm number | The value indicates the most severe current alarm | 43641 |  | u16 | 1 | 0 | 0 | 0 | R
EB107-EP15-BT3 Return temp. | Return temperature | 43662 | °C | s16 | 10 | 0 | 0 | 0 | R
EB107-EP15-BT10 Brine in temp |  | 43663 | °C | s16 | 10 | 0 | 0 | 0 | R
EB107-EP15-BT11 Brine out temp |  | 43664 | °C | s16 | 10 | 0 | 0 | 0 | R
EB107-EP15-BT12 Cond. out |  | 43665 | °C | s16 | 10 | 0 | 0 | 0 | R
EB107-EP15-BT14 Hot gas temp |  | 43666 | °C | s16 | 10 | 0 | 0 | 0 | R
EB107-EP15-BT15 Liquid line |  | 43667 | °C | s16 | 10 | 0 | 0 | 0 | R
EB107-EP15-BT17 Suction |  | 43668 | °C | s16 | 10 | 0 | 0 | 0 | R
EB107-EP15-BT29 Compr. Oil. temp. |  | 43669 | °C | s16 | 10 | 0 | 0 | 0 | R
EB107-EP15-BP8 Pressure transmitter |  | 43670 | °C | s16 | 10 | 0 | 0 | 0 | R
EB107-EP15 Compressor State |  | 43671 |  | u8 | 1 | 0 | 0 | 0 | R
EB107-EP15 Compr. time to start |  | 43672 |  | u8 | 1 | 0 | 0 | 0 | R
EB107-EP15 Relay status |  | 43673 |  | u16 | 1 | 0 | 0 | 0 | R
EB107-EP15 Heat med. pump status |  | 43674 |  | u8 | 1 | 0 | 0 | 0 | R
EB107-EP15 Brine pump status |  | 43675 |  | u8 | 1 | 0 | 0 | 0 | R
EB107-EP15 Compressor starts |  | 43676 |  | u32 | 1 | 0 | 0 | 0 | R
EB107-EP15 Tot. op.time compr |  | 43678 | h | u32 | 1 | 0 | 0 | 0 | R
EB107-EP15 Tot. HW op.time compr |  | 43680 | h | u32 | 1 | 0 | 0 | 0 | R
EB107-EP15 Alarm number | The value indicates the most severe current alarm | 43682 |  | u16 | 1 | 0 | 0 | 0 | R
EB107-EP14-BT3 Return temp. | Return temperature | 43683 | °C | s16 | 10 | 0 | 0 | 0 | R
EB107-EP14-BT10 Brine in temp |  | 43684 | °C | s16 | 10 | 0 | 0 | 0 | R
EB107-EP14-BT11 Brine out temp |  | 43685 | °C | s16 | 10 | 0 | 0 | 0 | R
EB107-EP14-BT12 Cond. out |  | 43686 | °C | s16 | 10 | 0 | 0 | 0 | R
EB107-EP14-BT14 Hot gas temp |  | 43687 | °C | s16 | 10 | 0 | 0 | 0 | R
EB107-EP14-BT15 Liquid line |  | 43688 | °C | s16 | 10 | 0 | 0 | 0 | R
EB107-EP14-BT17 Suction |  | 43689 | °C | s16 | 10 | 0 | 0 | 0 | R
EB107-EP14-BT29 Compr. Oil. temp. |  | 43690 | °C | s16 | 10 | 0 | 0 | 0 | R
EB107-EP14-BP8 Pressure transmitter |  | 43691 | °C | s16 | 10 | 0 | 0 | 0 | R
EB107-EP14 Compressor State |  | 43692 |  | u8 | 1 | 0 | 0 | 0 | R
EB107-EP14 Compr. time to start |  | 43693 |  | u8 | 1 | 0 | 0 | 0 | R
EB107-EP14 Relay status |  | 43694 |  | u16 | 1 | 0 | 0 | 0 | R
EB107-EP14 Heat med. pump status |  | 43695 |  | u8 | 1 | 0 | 0 | 0 | R
EB107-EP14 Brine pump status |  | 43696 |  | u8 | 1 | 0 | 0 | 0 | R
EB107-EP14 Compressor starts |  | 43697 |  | u32 | 1 | 0 | 0 | 0 | R
EB107-EP14 Tot. op.time compr |  | 43699 | h | u32 | 1 | 0 | 0 | 0 | R
EB107-EP14 Tot. HW op.time compr |  | 43701 | h | u32 | 1 | 0 | 0 | 0 | R
EB107-EP14 Alarm number | The value indicates the most severe current alarm | 43703 |  | u16 | 1 | 0 | 0 | 0 | R
EB106-EP15-BT3 Return temp. | Return temperature | 43724 | °C | s16 | 10 | 0 | 0 | 0 | R
EB106-EP15-BT10 Brine in temp |  | 43725 | °C | s16 | 10 | 0 | 0 | 0 | R
EB106-EP15-BT11 Brine out temp |  | 43726 | °C | s16 | 10 | 0 | 0 | 0 | R
EB106-EP15-BT12 Cond. out |  | 43727 | °C | s16 | 10 | 0 | 0 | 0 | R
EB106-EP15-BT14 Hot gas temp |  | 43728 | °C | s16 | 10 | 0 | 0 | 0 | R
EB106-EP15-BT15 Liquid line |  | 43729 | °C | s16 | 10 | 0 | 0 | 0 | R
EB106-EP15-BT17 Suction |  | 43730 | °C | s16 | 10 | 0 | 0 | 0 | R
EB106-EP15-BT29 Compr. Oil. temp. |  | 43731 | °C | s16 | 10 | 0 | 0 | 0 | R
EB106-EP15-BP8 Pressure transmitter |  | 43732 | °C | s16 | 10 | 0 | 0 | 0 | R
EB106-EP15 Compressor State |  | 43733 |  | u8 | 1 | 0 | 0 | 0 | R
EB106-EP15 Compr. time to start |  | 43734 |  | u8 | 1 | 0 | 0 | 0 | R
EB106-EP15 Relay status |  | 43735 |  | u16 | 1 | 0 | 0 | 0 | R
EB106-EP15 Heat med. pump status |  | 43736 |  | u8 | 1 | 0 | 0 | 0 | R
EB106-EP15 Brine pump status |  | 43737 |  | u8 | 1 | 0 | 0 | 0 | R
EB106-EP15 Compressor starts |  | 43738 |  | u32 | 1 | 0 | 0 | 0 | R
EB106-EP15 Tot. op.time compr |  | 43740 | h | u32 | 1 | 0 | 0 | 0 | R
EB106-EP15 Tot. HW op.time compr |  | 43742 | h | u32 | 1 | 0 | 0 | 0 | R
EB106-EP15 Alarm number | The value indicates the most severe current alarm | 43744 |  | u16 | 1 | 0 | 0 | 0 | R
EB106-EP14-BT3 Return temp. | Return temperature | 43745 | °C | s16 | 10 | 0 | 0 | 0 | R
EB106-EP14-BT10 Brine in temp |  | 43746 | °C | s16 | 10 | 0 | 0 | 0 | R
EB106-EP14-BT11 Brine out temp |  | 43747 | °C | s16 | 10 | 0 | 0 | 0 | R
EB106-EP14-BT12 Cond. out |  | 43748 | °C | s16 | 10 | 0 | 0 | 0 | R
EB106-EP14-BT14 Hot gas temp |  | 43749 | °C | s16 | 10 | 0 | 0 | 0 | R
EB106-EP14-BT15 Liquid line |  | 43750 | °C | s16 | 10 | 0 | 0 | 0 | R
EB106-EP14-BT17 Suction |  | 43751 | °C | s16 | 10 | 0 | 0 | 0 | R
EB106-EP14-BT29 Compr. Oil. temp. |  | 43752 | °C | s16 | 10 | 0 | 0 | 0 | R
EB106-EP14-BP8 Pressure transmitter |  | 43753 | °C | s16 | 10 | 0 | 0 | 0 | R
EB106-EP14 Compressor State |  | 43754 |  | u8 | 1 | 0 | 0 | 0 | R
EB106-EP14 Compr. time to start |  | 43755 |  | u8 | 1 | 0 | 0 | 0 | R
EB106-EP14 Relay status |  | 43756 |  | u16 | 1 | 0 | 0 | 0 | R
EB106-EP14 Heat med. pump status |  | 43757 |  | u8 | 1 | 0 | 0 | 0 | R
EB106-EP14 Brine pump status |  | 43758 |  | u8 | 1 | 0 | 0 | 0 | R
EB106-EP14 Compressor starts |  | 43759 |  | u32 | 1 | 0 | 0 | 0 | R
EB106-EP14 Tot. op.time compr |  | 43761 | h | u32 | 1 | 0 | 0 | 0 | R
EB106-EP14 Tot. HW op.time compr |  | 43763 | h | u32 | 1 | 0 | 0 | 0 | R
EB106-EP14 Alarm number | The value indicates the most severe current alarm | 43765 |  | u16 | 1 | 0 | 0 | 0 | R
EB105-EP15-BT3 Return temp. | Return temperature | 43786 | °C | s16 | 10 | 0 | 0 | 0 | R
EB105-EP15-BT10 Brine in temp |  | 43787 | °C | s16 | 10 | 0 | 0 | 0 | R
EB105-EP15-BT11 Brine out temp |  | 43788 | °C | s16 | 10 | 0 | 0 | 0 | R
EB105-EP15-BT12 Cond. out |  | 43789 | °C | s16 | 10 | 0 | 0 | 0 | R
EB105-EP15-BT14 Hot gas temp |  | 43790 | °C | s16 | 10 | 0 | 0 | 0 | R
EB105-EP15-BT15 Liquid line |  | 43791 | °C | s16 | 10 | 0 | 0 | 0 | R
EB105-EP15-BT17 Suction |  | 43792 | °C | s16 | 10 | 0 | 0 | 0 | R
EB105-EP15-BT29 Compr. Oil. temp. |  | 43793 | °C | s16 | 10 | 0 | 0 | 0 | R
EB105-EP15-BP8 Pressure transmitter |  | 43794 | °C | s16 | 10 | 0 | 0 | 0 | R
EB105-EP15 Compressor State |  | 43795 |  | u8 | 1 | 0 | 0 | 0 | R
EB105-EP15 Compr. time to start |  | 43796 |  | u8 | 1 | 0 | 0 | 0 | R
EB105-EP15 Relay status |  | 43797 |  | u16 | 1 | 0 | 0 | 0 | R
EB105-EP15 Heat med. pump status |  | 43798 |  | u8 | 1 | 0 | 0 | 0 | R
EB105-EP15 Brine pump status |  | 43799 |  | u8 | 1 | 0 | 0 | 0 | R
EB105-EP15 Compressor starts |  | 43800 |  | u32 | 1 | 0 | 0 | 0 | R
EB105-EP15 Tot. op.time compr |  | 43802 | h | u32 | 1 | 0 | 0 | 0 | R
EB105-EP15 Tot. HW op.time compr |  | 43804 | h | u32 | 1 | 0 | 0 | 0 | R
EB105-EP15 Alarm number | The value indicates the most severe current alarm | 43806 |  | u16 | 1 | 0 | 0 | 0 | R
EB105-EP14-BT3 Return temp. | Return temperature | 43807 | °C | s16 | 10 | 0 | 0 | 0 | R
EB105-EP14-BT10 Brine in temp |  | 43808 | °C | s16 | 10 | 0 | 0 | 0 | R
EB105-EP14-BT11 Brine out temp |  | 43809 | °C | s16 | 10 | 0 | 0 | 0 | R
EB105-EP14-BT12 Cond. out |  | 43810 | °C | s16 | 10 | 0 | 0 | 0 | R
EB105-EP14-BT14 Hot gas temp |  | 43811 | °C | s16 | 10 | 0 | 0 | 0 | R
EB105-EP14-BT15 Liquid line |  | 43812 | °C | s16 | 10 | 0 | 0 | 0 | R
EB105-EP14-BT17 Suction |  | 43813 | °C | s16 | 10 | 0 | 0 | 0 | R
EB105-EP14-BT29 Compr. Oil. temp. |  | 43814 | °C | s16 | 10 | 0 | 0 | 0 | R
EB105-EP14-BP8 Pressure transmitter |  | 43815 | °C | s16 | 10 | 0 | 0 | 0 | R
EB105-EP14 Compressor State |  | 43816 |  | u8 | 1 | 0 | 0 | 0 | R
EB105-EP14 Compr. time to start |  | 43817 |  | u8 | 1 | 0 | 0 | 0 | R
EB105-EP14 Relay status |  | 43818 |  | u16 | 1 | 0 | 0 | 0 | R
EB105-EP14 Heat med. pump status |  | 43819 |  | u8 | 1 | 0 | 0 | 0 | R
EB105-EP14 Brine pump status |  | 43820 |  | u8 | 1 | 0 | 0 | 0 | R
EB105-EP14 Compressor starts |  | 43821 |  | u32 | 1 | 0 | 0 | 0 | R
EB105-EP14 Tot. op.time compr |  | 43823 | h | u32 | 1 | 0 | 0 | 0 | R
EB105-EP14 Tot. HW op.time compr |  | 43825 | h | u32 | 1 | 0 | 0 | 0 | R
EB105-EP14 Alarm number | The value indicates the most severe current alarm | 43827 |  | u16 | 1 | 0 | 0 | 0 | R
EB104-EP15-BT3 Return temp. | Return temperature | 43848 | °C | s16 | 10 | 0 | 0 | 0 | R
EB104-EP15-BT10 Brine in temp |  | 43849 | °C | s16 | 10 | 0 | 0 | 0 | R
EB104-EP15-BT11 Brine out temp |  | 43850 | °C | s16 | 10 | 0 | 0 | 0 | R
EB104-EP15-BT12 Cond. out |  | 43851 | °C | s16 | 10 | 0 | 0 | 0 | R
EB104-EP15-BT14 Hot gas temp |  | 43852 | °C | s16 | 10 | 0 | 0 | 0 | R
EB104-EP15-BT15 Liquid line |  | 43853 | °C | s16 | 10 | 0 | 0 | 0 | R
EB104-EP15-BT17 Suction |  | 43854 | °C | s16 | 10 | 0 | 0 | 0 | R
EB104-EP15-BT29 Compr. Oil. temp. |  | 43855 | °C | s16 | 10 | 0 | 0 | 0 | R
EB104-EP15-BP8 Pressure transmitter |  | 43856 | °C | s16 | 10 | 0 | 0 | 0 | R
EB104-EP15 Compressor State |  | 43857 |  | u8 | 1 | 0 | 0 | 0 | R
EB104-EP15 Compr. time to start |  | 43858 |  | u8 | 1 | 0 | 0 | 0 | R
EB104-EP15 Relay status |  | 43859 |  | u16 | 1 | 0 | 0 | 0 | R
EB104-EP15 Heat med. pump status |  | 43860 |  | u8 | 1 | 0 | 0 | 0 | R
EB104-EP15 Brine pump status |  | 43861 |  | u8 | 1 | 0 | 0 | 0 | R
EB104-EP15 Compressor starts |  | 43862 |  | u32 | 1 | 0 | 0 | 0 | R
EB104-EP15 Tot. op.time compr |  | 43864 | h | u32 | 1 | 0 | 0 | 0 | R
EB104-EP15 Tot. HW op.time compr |  | 43866 | h | u32 | 1 | 0 | 0 | 0 | R
EB104-EP15 Alarm number | The value indicates the most severe current alarm | 43868 |  | u16 | 1 | 0 | 0 | 0 | R
EB104-EP14-BT3 Return temp. | Return temperature | 43869 | °C | s16 | 10 | 0 | 0 | 0 | R
EB104-EP14-BT10 Brine in temp |  | 43870 | °C | s16 | 10 | 0 | 0 | 0 | R
EB104-EP14-BT11 Brine out temp |  | 43871 | °C | s16 | 10 | 0 | 0 | 0 | R
EB104-EP14-BT12 Cond. out |  | 43872 | °C | s16 | 10 | 0 | 0 | 0 | R
EB104-EP14-BT14 Hot gas temp |  | 43873 | °C | s16 | 10 | 0 | 0 | 0 | R
EB104-EP14-BT15 Liquid line |  | 43874 | °C | s16 | 10 | 0 | 0 | 0 | R
EB104-EP14-BT17 Suction |  | 43875 | °C | s16 | 10 | 0 | 0 | 0 | R
EB104-EP14-BT29 Compr. Oil. temp. |  | 43876 | °C | s16 | 10 | 0 | 0 | 0 | R
EB104-EP14-BP8 Pressure transmitter |  | 43877 | °C | s16 | 10 | 0 | 0 | 0 | R
EB104-EP14 Compressor State |  | 43878 |  | u8 | 1 | 0 | 0 | 0 | R
EB104-EP14 Compr. time to start |  | 43879 |  | u8 | 1 | 0 | 0 | 0 | R
EB104-EP14 Relay status |  | 43880 |  | u16 | 1 | 0 | 0 | 0 | R
EB104-EP14 Heat med. pump status |  | 43881 |  | u8 | 1 | 0 | 0 | 0 | R
EB104-EP14 Brine pump status |  | 43882 |  | u8 | 1 | 0 | 0 | 0 | R
EB104-EP14 Compressor starts |  | 43883 |  | u32 | 1 | 0 | 0 | 0 | R
EB104-EP14 Tot. op.time compr |  | 43885 | h | u32 | 1 | 0 | 0 | 0 | R
EB104-EP14 Tot. HW op.time compr |  | 43887 | h | u32 | 1 | 0 | 0 | 0 | R
EB104-EP14 Alarm number | The value indicates the most severe current alarm | 43889 |  | u16 | 1 | 0 | 0 | 0 | R
EB103-EP15-BT3 Return temp. | Return temperature | 43910 | °C | s16 | 10 | 0 | 0 | 0 | R
EB103-EP15-BT10 Brine in temp |  | 43911 | °C | s16 | 10 | 0 | 0 | 0 | R
EB103-EP15-BT11 Brine out temp |  | 43912 | °C | s16 | 10 | 0 | 0 | 0 | R
EB103-EP15-BT12 Cond. out |  | 43913 | °C | s16 | 10 | 0 | 0 | 0 | R
EB103-EP15-BT14 Hot gas temp |  | 43914 | °C | s16 | 10 | 0 | 0 | 0 | R
EB103-EP15-BT15 Liquid line |  | 43915 | °C | s16 | 10 | 0 | 0 | 0 | R
EB103-EP15-BT17 Suction |  | 43916 | °C | s16 | 10 | 0 | 0 | 0 | R
EB103-EP15-BT29 Compr. Oil. temp. |  | 43917 | °C | s16 | 10 | 0 | 0 | 0 | R
EB103-EP15-BP8 Pressure transmitter |  | 43918 | °C | s16 | 10 | 0 | 0 | 0 | R
EB103-EP15 Compressor State |  | 43919 |  | u8 | 1 | 0 | 0 | 0 | R
EB103-EP15 Compr. time to start |  | 43920 |  | u8 | 1 | 0 | 0 | 0 | R
EB103-EP15 Relay status |  | 43921 |  | u16 | 1 | 0 | 0 | 0 | R
EB103-EP15 Heat med. pump status |  | 43922 |  | u8 | 1 | 0 | 0 | 0 | R
EB103-EP15 Brine pump status |  | 43923 |  | u8 | 1 | 0 | 0 | 0 | R
EB103-EP15 Compressor starts |  | 43924 |  | u32 | 1 | 0 | 0 | 0 | R
EB103-EP15 Tot. op.time compr |  | 43926 | h | u32 | 1 | 0 | 0 | 0 | R
EB103-EP15 Tot. HW op.time compr |  | 43928 | h | u32 | 1 | 0 | 0 | 0 | R
EB103-EP15 Alarm number | The value indicates the most severe current alarm | 43930 |  | u16 | 1 | 0 | 0 | 0 | R
EB103-EP14-BT3 Return temp. | Return temperature | 43931 | °C | s16 | 10 | 0 | 0 | 0 | R
EB103-EP14-BT10 Brine in temp |  | 43932 | °C | s16 | 10 | 0 | 0 | 0 | R
EB103-EP14-BT11 Brine out temp |  | 43933 | °C | s16 | 10 | 0 | 0 | 0 | R
EB103-EP14-BT12 Cond. out |  | 43934 | °C | s16 | 10 | 0 | 0 | 0 | R
EB103-EP14-BT14 Hot gas temp |  | 43935 | °C | s16 | 10 | 0 | 0 | 0 | R
EB103-EP14-BT15 Liquid line |  | 43936 | °C | s16 | 10 | 0 | 0 | 0 | R
EB103-EP14-BT17 Suction |  | 43937 | °C | s16 | 10 | 0 | 0 | 0 | R
EB103-EP14-BT29 Compr. Oil. temp. |  | 43938 | °C | s16 | 10 | 0 | 0 | 0 | R
EB103-EP14-BP8 Pressure transmitter |  | 43939 | °C | s16 | 10 | 0 | 0 | 0 | R
EB103-EP14 Compressor State |  | 43940 |  | u8 | 1 | 0 | 0 | 0 | R
EB103-EP14 Compr. time to start |  | 43941 |  | u8 | 1 | 0 | 0 | 0 | R
EB103-EP14 Relay status |  | 43942 |  | u16 | 1 | 0 | 0 | 0 | R
EB103-EP14 Heat med. pump status |  | 43943 |  | u8 | 1 | 0 | 0 | 0 | R
EB103-EP14 Brine pump status |  | 43944 |  | u8 | 1 | 0 | 0 | 0 | R
EB103-EP14 Compressor starts |  | 43945 |  | u32 | 1 | 0 | 0 | 0 | R
EB103-EP14 Tot. op.time compr |  | 43947 | h | u32 | 1 | 0 | 0 | 0 | R
EB103-EP14 Tot. HW op.time compr |  | 43949 | h | u32 | 1 | 0 | 0 | 0 | R
EB103-EP14 Alarm number | The value indicates the most severe current alarm | 43951 |  | u16 | 1 | 0 | 0 | 0 | R
EB102-EP15-BT3 Return temp. | Return temperature | 43972 | °C | s16 | 10 | 0 | 0 | 0 | R
EB102-EP15-BT10 Brine in temp |  | 43973 | °C | s16 | 10 | 0 | 0 | 0 | R
EB102-EP15-BT11 Brine out temp |  | 43974 | °C | s16 | 10 | 0 | 0 | 0 | R
EB102-EP15-BT12 Cond. out |  | 43975 | °C | s16 | 10 | 0 | 0 | 0 | R
EB102-EP15-BT14 Hot gas temp |  | 43976 | °C | s16 | 10 | 0 | 0 | 0 | R
EB102-EP15-BT15 Liquid line |  | 43977 | °C | s16 | 10 | 0 | 0 | 0 | R
EB102-EP15-BT17 Suction |  | 43978 | °C | s16 | 10 | 0 | 0 | 0 | R
EB102-EP15-BT29 Compr. Oil. temp. |  | 43979 | °C | s16 | 10 | 0 | 0 | 0 | R
EB102-EP15-BP8 Pressure transmitter |  | 43980 | °C | s16 | 10 | 0 | 0 | 0 | R
EB102-EP15 Compressor State |  | 43981 |  | u8 | 1 | 0 | 0 | 0 | R
EB102-EP15 Compr. time to start |  | 43982 |  | u8 | 1 | 0 | 0 | 0 | R
EB102-EP15 Relay status |  | 43983 |  | u16 | 1 | 0 | 0 | 0 | R
EB102-EP15 Heat med. pump status |  | 43984 |  | u8 | 1 | 0 | 0 | 0 | R
EB102-EP15 Brine pump status |  | 43985 |  | u8 | 1 | 0 | 0 | 0 | R
EB102-EP15 Compressor starts |  | 43986 |  | u32 | 1 | 0 | 0 | 0 | R
EB102-EP15 Tot. op.time compr |  | 43988 | h | u32 | 1 | 0 | 0 | 0 | R
EB102-EP15 Tot. HW op.time compr |  | 43990 | h | u32 | 1 | 0 | 0 | 0 | R
EB102-EP15 Alarm number | The value indicates the most severe current alarm | 43992 |  | u16 | 1 | 0 | 0 | 0 | R
EB102-EP14-BT3 Return temp. | Return temperature | 43993 | °C | s16 | 10 | 0 | 0 | 0 | R
EB102-EP14-BT10 Brine in temp |  | 43994 | °C | s16 | 10 | 0 | 0 | 0 | R
EB102-EP14-BT11 Brine out temp |  | 43995 | °C | s16 | 10 | 0 | 0 | 0 | R
EB102-EP14-BT12 Cond. out |  | 43996 | °C | s16 | 10 | 0 | 0 | 0 | R
EB102-EP14-BT14 Hot gas temp |  | 43997 | °C | s16 | 10 | 0 | 0 | 0 | R
EB102-EP14-BT15 Liquid line |  | 43998 | °C | s16 | 10 | 0 | 0 | 0 | R
EB102-EP14-BT17 Suction |  | 43999 | °C | s16 | 10 | 0 | 0 | 0 | R
EB102-EP14-BT29 Compr. Oil. temp. |  | 44000 | °C | s16 | 10 | 0 | 0 | 0 | R
EB102-EP14-BP8 Pressure transmitter |  | 44001 | °C | s16 | 10 | 0 | 0 | 0 | R
EB102-EP14 Compressor State |  | 44002 |  | u8 | 1 | 0 | 0 | 0 | R
EB102-EP14 Compr. time to start |  | 44003 |  | u8 | 1 | 0 | 0 | 0 | R
EB102-EP14 Relay status |  | 44004 |  | u16 | 1 | 0 | 0 | 0 | R
EB102-EP14 Heat med. pump status |  | 44005 |  | u8 | 1 | 0 | 0 | 0 | R
EB102-EP14 Brine pump status |  | 44006 |  | u8 | 1 | 0 | 0 | 0 | R
EB102-EP14 Compressor starts |  | 44007 |  | u32 | 1 | 0 | 0 | 0 | R
EB102-EP14 Tot. op.time compr |  | 44009 | h | u32 | 1 | 0 | 0 | 0 | R
EB102-EP14 Tot. HW op.time compr |  | 44011 | h | u32 | 1 | 0 | 0 | 0 | R
EB102-EP14 Alarm number | The value indicates the most severe current alarm | 44013 |  | u16 | 1 | 0 | 0 | 0 | R
EB101-EP15-BT3 Return temp. | Return temperature | 44034 | °C | s16 | 10 | 0 | 0 | 0 | R
EB101-EP15-BT10 Brine in temp |  | 44035 | °C | s16 | 10 | 0 | 0 | 0 | R
EB101-EP15-BT11 Brine out temp |  | 44036 | °C | s16 | 10 | 0 | 0 | 0 | R
EB101-EP15-BT12 Cond. out |  | 44037 | °C | s16 | 10 | 0 | 0 | 0 | R
EB101-EP15-BT14 Hot gas temp |  | 44038 | °C | s16 | 10 | 0 | 0 | 0 | R
EB101-EP15-BT15 Liquid line |  | 44039 | °C | s16 | 10 | 0 | 0 | 0 | R
EB101-EP15-BT17 Suction |  | 44040 | °C | s16 | 10 | 0 | 0 | 0 | R
EB101-EP15-BT29 Compr. Oil. temp. |  | 44041 | °C | s16 | 10 | 0 | 0 | 0 | R
EB101-EP15-BP8 Pressure transmitter |  | 44042 | °C | s16 | 10 | 0 | 0 | 0 | R
EB101-EP15 Compressor State |  | 44043 |  | u8 | 1 | 0 | 0 | 0 | R
EB101-EP15 Compr. time to start |  | 44044 |  | u8 | 1 | 0 | 0 | 0 | R
EB101-EP15 Relay status |  | 44045 |  | u16 | 1 | 0 | 0 | 0 | R
EB101-EP15 Heat med. pump status |  | 44046 |  | u8 | 1 | 0 | 0 | 0 | R
EB101-EP15 Brine pump status |  | 44047 |  | u8 | 1 | 0 | 0 | 0 | R
EB101-EP15 Compressor starts |  | 44048 |  | u32 | 1 | 0 | 0 | 0 | R
EB101-EP15 Tot. op.time compr |  | 44050 | h | u32 | 1 | 0 | 0 | 0 | R
EB101-EP15 Tot. HW op.time compr |  | 44052 | h | u32 | 1 | 0 | 0 | 0 | R
EB101-EP15 Alarm number | The value indicates the most severe current alarm | 44054 |  | u16 | 1 | 0 | 0 | 0 | R
EB101-EP14-BT3 Return temp. | Return temperature | 44055 | °C | s16 | 10 | 0 | 0 | 0 | R
EB101-EP14-BT10 Brine in temp |  | 44056 | °C | s16 | 10 | 0 | 0 | 0 | R
EB101-EP14-BT11 Brine out temp |  | 44057 | °C | s16 | 10 | 0 | 0 | 0 | R
EB101-EP14-BT12 Cond. out |  | 44058 | °C | s16 | 10 | 0 | 0 | 0 | R
EB101-EP14-BT14 Hot gas temp |  | 44059 | °C | s16 | 10 | 0 | 0 | 0 | R
EB101-EP14-BT15 Liquid line |  | 44060 | °C | s16 | 10 | 0 | 0 | 0 | R
EB101-EP14-BT17 Suction |  | 44061 | °C | s16 | 10 | 0 | 0 | 0 | R
EB101-EP14-BT29 Compr. Oil. temp. |  | 44062 | °C | s16 | 10 | 0 | 0 | 0 | R
EB101-EP14-BP8 Pressure transmitter |  | 44063 | °C | s16 | 10 | 0 | 0 | 0 | R
EB101-EP14 Compressor State |  | 44064 |  | u8 | 1 | 0 | 0 | 0 | R
EB101-EP14 Compr. time to start |  | 44065 |  | u8 | 1 | 0 | 0 | 0 | R
EB101-EP14 Relay status |  | 44066 |  | u16 | 1 | 0 | 0 | 0 | R
EB101-EP14 Heat med. pump status |  | 44067 |  | u8 | 1 | 0 | 0 | 0 | R
EB101-EP14 Brine pump status |  | 44068 |  | u8 | 1 | 0 | 0 | 0 | R
EB101-EP14 Compressor starts |  | 44069 |  | u32 | 1 | 0 | 0 | 0 | R
EB101-EP14 Tot. op.time compr |  | 44071 | h | u32 | 1 | 0 | 0 | 0 | R
EB101-EP14 Tot. HW op.time compr |  | 44073 | h | u32 | 1 | 0 | 0 | 0 | R
EB101-EP14 Alarm number | The value indicates the most severe current alarm | 44075 |  | u16 | 1 | 0 | 0 | 0 | R
EB108-EP15 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2 | 44138 |  | u8 | 1 | 0 | 0 | 0 | R
EB108-EP14 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2 | 44139 |  | u8 | 1 | 0 | 0 | 0 | R
EB107-EP15 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2 | 44151 |  | u8 | 1 | 0 | 0 | 0 | R
EB107-EP14 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2 | 44152 |  | u8 | 1 | 0 | 0 | 0 | R
EB106-EP15 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2 | 44164 |  | u8 | 1 | 0 | 0 | 0 | R
EB106-EP14 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2 | 44165 |  | u8 | 1 | 0 | 0 | 0 | R
EB105-EP15 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2 | 44177 |  | u8 | 1 | 0 | 0 | 0 | R
EB105-EP14 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2 | 44178 |  | u8 | 1 | 0 | 0 | 0 | R
EB104-EP15 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2 | 44190 |  | u8 | 1 | 0 | 0 | 0 | R
EB104-EP14 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2 | 44191 |  | u8 | 1 | 0 | 0 | 0 | R
EB103-EP15 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2 | 44203 |  | u8 | 1 | 0 | 0 | 0 | R
EB103-EP14 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2 | 44204 |  | u8 | 1 | 0 | 0 | 0 | R
EB102-EP15 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2 | 44216 |  | u8 | 1 | 0 | 0 | 0 | R
EB102-EP14 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2 | 44217 |  | u8 | 1 | 0 | 0 | 0 | R
EB101-EP15 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2 | 44229 |  | u8 | 1 | 0 | 0 | 0 | R
EB101-EP14 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2 | 44230 |  | u8 | 1 | 0 | 0 | 0 | R
EB100-EP15 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2 | 44242 |  | u8 | 1 | 0 | 0 | 0 | R
EB100-EP14 Prio | Indicates what need is assigned to the compressor module, 0 = Off, 1 = Heat, 2 = Hot water, 3 = Pool 1, 4 = Pool2 | 44243 |  | u8 | 1 | 0 | 0 | 0 | R
Cool Degree Minutes |  | 44266 |  | s16 | 10 | -30000 | 30000 | 0 | R/W
Calc. Cooling Supply Temperature S4 |  | 44267 | °C | s16 | 10 | 0 | 0 | 0 | R
Calc. Cooling Supply Temperature S3 |  | 44268 | °C | s16 | 10 | 0 | 0 | 0 | R
Calc. Cooling Supply Temperature S2 |  | 44269 | °C | s16 | 10 | 0 | 0 | 0 | R
Calc. Cooling Supply Temperature S1 |  | 44270 | °C | s16 | 10 | 0 | 0 | 0 | R
State ACS | The state of the ACS accessory | 44276 |  | u8 | 1 | 0 | 0 | 0 | R
State ACS heatdump | The state of the heatdump in the ACS accessory | 44277 |  | u8 | 1 | 0 | 0 | 0 | R
State ACS cooldump | The state of the cooldump in the ACS accessory | 44278 |  | u8 | 1 | 0 | 0 | 0 | R
Used cprs. HW | The number of compressors that's currently producing hot water | 44282 |  | u8 | 1 | 0 | 0 | 0 | R
Used cprs. heat | The number of compressors that's currently producing heating | 44283 |  | u8 | 1 | 0 | 0 | 0 | R
Used cprs. pool 1 | The number of compressors that's currently producing poolheating for pool 1 | 44284 |  | u8 | 1 | 0 | 0 | 0 | R
Used cprs. pool 2 | The number of compressors that's currently producing poolheating for pool 2 | 44285 |  | u8 | 1 | 0 | 0 | 0 | R
Used cprs. cool | The number of compressors that's currently producing active cooling | 44320 |  | u8 | 1 | 0 | 0 | 0 | R
Software release |  | 44331 |  | u8 | 1 | 0 | 0 | 0 | R
Alarm number | The value indicates the most severe current alarm | 45001 |  | s16 | 1 | 0 | 0 | 0 | R
Floor drying timer |  | 47291 | hrs | u16 | 1 | 0 | 10000 | 0 | R
Heat curve S4 | Heat curve to use see manual for the different curves. | 47004 |  | s8 | 1 | 0 | 15 | 9 | R/W
Heat curve S3 | Heat curve to use see manual for the different curves. | 47005 |  | s8 | 1 | 0 | 15 | 9 | R/W
Heat curve S2 | Heat curve to use see manual for the different curves. | 47006 |  | s8 | 1 | 0 | 15 | 9 | R/W
Heat curve S1 | Heat curve to use see manual for the different curves. | 47007 |  | s8 | 1 | 0 | 15 | 9 | R/W
Offset S4 | Offset of the heat curve | 47008 |  | s8 | 1 | -10 | 10 | 0 | R/W
Offset S3 | Offset of the heat curve | 47009 |  | s8 | 1 | -10 | 10 | 0 | R/W
Offset S2 | Offset of the heat curve | 47010 |  | s8 | 1 | -10 | 10 | 0 | R/W
Offset S1 | Offset of the heat curve | 47011 |  | s8 | 1 | -10 | 10 | 0 | R/W
Min Supply System 4 |  | 47012 | °C | s16 | 10 | 50 | 700 | 200 | R/W
Min Supply System 3 |  | 47013 | °C | s16 | 10 | 50 | 700 | 200 | R/W
Min Supply System 2 |  | 47014 | °C | s16 | 10 | 50 | 700 | 200 | R/W
Min Supply System 1 |  | 47015 | °C | s16 | 10 | 50 | 700 | 200 | R/W
Max Supply System 4 |  | 47016 | °C | s16 | 10 | 50 | 700 | 600 | R/W
Max Supply System 3 |  | 47017 | °C | s16 | 10 | 50 | 700 | 600 | R/W
Max Supply System 2 |  | 47018 | °C | s16 | 10 | 50 | 700 | 600 | R/W
Max Supply System 1 |  | 47019 | °C | s16 | 10 | 50 | 700 | 600 | R/W
Own Curve P7 | User defined curve point | 47020 | °C | s8 | 1 | 0 | 80 | 15 | R/W
Own Curve P6 | User defined curve point | 47021 | °C | s8 | 1 | 0 | 80 | 15 | R/W
Own Curve P5 | User defined curve point | 47022 | °C | s8 | 1 | 0 | 80 | 26 | R/W
Own Curve P4 | User defined curve point | 47023 | °C | s8 | 1 | 0 | 80 | 32 | R/W
Own Curve P3 | User defined curve point | 47024 | °C | s8 | 1 | 0 | 80 | 35 | R/W
Own Curve P2 | User defined curve point | 47025 | °C | s8 | 1 | 0 | 80 | 40 | R/W
Own Curve P1 | User defined curve point | 47026 | °C | s8 | 1 | 0 | 80 | 45 | R/W
Point offset outdoor temp. | Outdoor temperature point where the heat curve is offset | 47027 | °C | s8 | 1 | -40 | 30 | 0 | R/W
Point offset | Amount of offset at the point offset temperature | 47028 | °C | s8 | 1 | -10 | 10 | 0 | R/W
External adjustment S4 | Change of the offset of the heat curve when closing the external adjustment input | 47029 |  | s8 | 1 | -10 | 10 | 0 | R/W
External adjustment S3 | Change of the offset of the heat curve when closing the external adjustment input | 47030 |  | s8 | 1 | -10 | 10 | 0 | R/W
External adjustment S2 | Change of the offset of the heat curve when closing the external adjustment input | 47031 |  | s8 | 1 | -10 | 10 | 0 | R/W
External adjustment S1 | Change of the offset of the heat curve when closing the external adjustment input | 47032 |  | s8 | 1 | -10 | 10 | 0 | R/W
External adjustment with room sensor S4 | Room temperature setting when closing the external adjustment input | 47033 | °C | s16 | 10 | 50 | 300 | 200 | R/W
External adjustment with room sensor S3 | Room temperature setting when closing the external adjustment input | 47034 | °C | s16 | 10 | 50 | 300 | 200 | R/W
External adjustment with room sensor S2 | Room temperature setting when closing the external adjustment input | 47035 | °C | s16 | 10 | 50 | 300 | 200 | R/W
External adjustment with room sensor S1 | Room temperature setting when closing the external adjustment input | 47036 | °C | s16 | 10 | 50 | 300 | 200 | R/W
Hot water mode | 0=Economy 1=Normal 2=Luxury | 47041 |  | s8 | 1 | 0 | 2 | 1 | R/W
Start temperature HW Luxury | Start temperature for heating water | 47043 | °C | s16 | 10 | 50 | 700 | 470 | R/W
Start temperature HW Normal | Start temperature for heating water | 47044 | °C | s16 | 10 | 50 | 700 | 450 | R/W
Start temperature HW Economy | Start temperature for heating water | 47045 | °C | s16 | 10 | 50 | 700 | 380 | R/W
Stop temperature Periodic HW | Temperature where hot water generation will stop | 47046 | °C | s16 | 10 | 550 | 700 | 550 | R/W
Stop temperature HW Luxury | Temperature where hot water generation will stop | 47047 | °C | s16 | 10 | 50 | 700 | 520 | R/W
Stop temperature HW Normal | Temperature where hot water generation will stop | 47048 | °C | s16 | 10 | 50 | 700 | 500 | R/W
Stop temperature HW Economy | Temperature where hot water generation will stop | 47049 | °C | s16 | 10 | 50 | 700 | 430 | R/W
Periodic HW | Activates the periodic hot water generation | 47050 |  | s8 | 1 | 0 | 1 | 1 | R/W
Periodic HW Interval | Interval between Periodic hot water sessions | 47051 | days | s8 | 1 | 1 | 90 | 14 | R/W
Run time HWC | Run time for the hot water circulation system | 47054 | min | s8 | 1 | 1 | 60 | 3 | R/W
Still time HWC | Still time for the hot water circulation system | 47055 | min | s8 | 1 | 0 | 60 | 12 | R/W
Language | Display language in the heat pump 0=English 1=Svenska 2=Deutsch 3=Francais 4=Espanol 5=Suomi 6=Lietuviu 7=Cesky 8=Polski 9=Nederlands 10=Norsk 11=Dansk 12=Eesti 13=Latviesu 16=Magyar | 47131 |  | s8 | 1 | 0 | 18 | 0 | R/W
Period HW |  | 47134 | min | u8 | 1 | 0 | 180 | 20 | R/W
Period Heat |  | 47135 | min | u8 | 1 | 0 | 180 | 20 | R/W
Period Pool |  | 47136 | min | u8 | 1 | 0 | 180 | 20 | R/W
Operational mode heat medium pump | 10=Intermittent 20=Continous 30=Economy 40=Auto | 47138 |  | u8 | 1 | 10 | 40 | 40 | R/W
Operational mode brine medium pump | 10=Intermittent 20=Continuous 30=Economy 40=Auto | 47139 |  | u8 | 1 | 10 | 30 | 10 | R/W
DM start heating | The value the degree minutes needed to be reached for the pump to start heating | 47206 |  | s16 | 1 | -1000 | -30 | -60 | R/W
DM between add. steps | The number of degree minutes between start of each electric addition step | 47209 |  | s16 | 1 | 0 | 0 | 0 | R/W
DM start add. with shunt |  | 47210 |  | s16 | 1 | -2000 | -30 | -400 | R/W
Fuse | Size of the fuse that the HP is connected to | 47214 | A | u8 | 1 | 1 | 200 | 16 | R/W
Exhaust Fan speed 4 |  | 47261 | % | u8 | 1 | 0 | 100 | 100 | R/W
Exhaust Fan speed 3 |  | 47262 | % | u8 | 1 | 0 | 100 | 80 | R/W
Exhaust Fan speed 2 |  | 47263 | % | u8 | 1 | 0 | 100 | 30 | R/W
Exhaust Fan speed 1 |  | 47264 | % | u8 | 1 | 0 | 100 | 0 | R/W
Exhaust Fan speed normal |  | 47265 | % | u8 | 1 | 0 | 100 | 65 | R/W
Fan return time 4 | Time from a changed fan speed until it returns to normal speed | 47271 | h | u8 | 1 | 1 | 99 | 4 | R/W
Fan return time 3 | Time from a changed fan speed until it returns to normal speed | 47272 | h | u8 | 1 | 1 | 99 | 4 | R/W
Fan return time 2 | Time from a changed fan speed until it returns to normal speed | 47273 | h | u8 | 1 | 1 | 99 | 4 | R/W
Fan return time 1 | Time from a changed fan speed until it returns to normal speed | 47274 | h | u8 | 1 | 1 | 99 | 4 | R/W
Filter Reminder period | Time between the reminder of filter replacement/cleaning. | 47275 | Months | u8 | 1 | 1 | 24 | 3 | R/W
Floor drying | 0=Off 1=On | 47276 |  | u8 | 1 | 0 | 1 | 0 | R/W
Floor drying period 7 | Days each period is active | 47277 | days | u8 | 1 | 0 | 30 | 2 | R/W
Floor drying period 6 | Days each period is active | 47278 | days | u8 | 1 | 0 | 30 | 2 | R/W
Floor drying period 5 | Days each period is active | 47279 | days | u8 | 1 | 0 | 30 | 2 | R/W
Floor drying period 4 | Days each period is active | 47280 | days | u8 | 1 | 0 | 30 | 3 | R/W
Floor drying period 3 | Days each period is active | 47281 | days | u8 | 1 | 0 | 30 | 2 | R/W
Floor drying period 2 | Days each period is active | 47282 | days | u8 | 1 | 0 | 30 | 2 | R/W
Floor drying period 1 | Days each period is active | 47283 | days | u8 | 1 | 0 | 30 | 2 | R/W
Floor drying temp. 7 | Supply temperature each period | 47284 | °C | u8 | 1 | 15 | 70 | 20 | R/W
Floor drying temp. 6 | Supply temperature each period | 47285 | °C | u8 | 1 | 15 | 70 | 30 | R/W
Floor drying temp. 5 | Supply temperature each period | 47286 | °C | u8 | 1 | 15 | 70 | 40 | R/W
Floor drying temp. 4 | Supply temperature each period | 47287 | °C | u8 | 1 | 15 | 70 | 45 | R/W
Floor drying temp. 3 | Supply temperature each period | 47288 | °C | u8 | 1 | 15 | 70 | 40 | R/W
Floor drying temp. 2 | Supply temperature each period | 47289 | °C | u8 | 1 | 15 | 70 | 30 | R/W
Floor drying temp. 1 | Supply temperature each period | 47290 | °C | u8 | 1 | 15 | 70 | 20 | R/W
Climate system 2 accessory | Activates the climate system 2 accessory 0=Off 1=On | 47302 |  | u8 | 1 | 0 | 1 | 0 | R/W
Climate system 3 accessory | Activates the climate system 3 accessory 0=Off 1=On | 47303 |  | u8 | 1 | 0 | 1 | 0 | R/W
Climate system 4 accessory | Activates the climate system 4 accessory 0=Off 1=On | 47304 |  | u8 | 1 | 0 | 1 | 0 | R/W
Climate system 4 mixing valve amp. | Mixing valve amplification for extra climate systems | 47305 |  | s8 | 10 | 1 | 100 | 10 | R/W
Climate system 3 mixing valve amp. | Mixing valve amplification for extra climate systems | 47306 |  | s8 | 10 | 1 | 100 | 10 | R/W
Climate system 2 mixing valve amp. | Mixing valve amplification for extra climate systems | 47307 |  | s8 | 10 | 1 | 100 | 10 | R/W
Climate system 4 shunt wait | Wait time between changes of the shunt in extra climate systems | 47308 | secs | s16 | 10 | 10 | 300 | 30 | R/W
Climate system 3 shunt wait | Wait time between changes of the shunt in extra climate systems | 47309 | secs | s16 | 10 | 10 | 300 | 30 | R/W
Climate system 2 shunt wait | Wait time between changes of the shunt in extra climate systems | 47310 | secs | s16 | 10 | 10 | 300 | 30 | R/W
FLM pump | Operating mode for the FLM pump 0=Off 1=On | 47312 |  | u8 | 1 | 0 | 1 | 0 | R/W
FLM defrost | Minimum time between defrost in FLM | 47313 | hrs | u8 | 1 | 1 | 30 | 10 | R/W
Shunt controlled add. accessory | Activates the shunt controlled addition accessory 0=Off 1=On | 47317 |  | u8 | 1 | 0 | 1 | 0 | R/W
Shunt controlled add. min. temp. |  | 47318 | °C | s8 | 1 | 5 | 90 | 55 | R/W
Shunt controlled add. min. runtime |  | 47319 | hrs | u8 | 1 | 0 | 48 | 12 | R/W
Shunt controlled add. mixing valve amp. | Mixing valve amplification for shunt controlled add. | 47320 |  | s8 | 10 | 1 | 100 | 10 | R/W
Shunt controlled add. mixing valve wait | Wait time between changes of the shunt in shunt controlled add. | 47321 | secs | s16 | 1 | 10 | 300 | 30 | R/W
Step controlled add. accessory | Activates the step controlled addition accessory 0=Off 1=On | 47322 |  | u8 | 1 | 0 | 1 | 0 | R/W
Step controlled add. diff. DM | Difference in DM of each step in the step controlled add. | 47324 |  | s16 | 1 | 0 | 1000 | 100 | R/W
Step controlled add. mode | Binary or linear stepping method. 0=Linear 1=Binary | 47326 |  | u8 | 1 | 0 | 1 | 0 | R/W
Ground water pump accessory | Ground water pump using AXC40 0=Off 1=On | 47327 |  | u8 | 1 | 0 | 1 | 0 | R/W
Cooling 2-pipe accessory | Activates the 2-pipe cooling accessory 0=Off 1=On | 47329 |  | u8 | 1 | 0 | 1 | 0 | R/W
Cooling 4-pipe accessory | Activates the 4-pipe cooling accessory 0=Off 1=On | 47330 |  | u8 | 1 | 0 | 1 | 0 | R/W
Time betw. switch heat/cool | Time between switching from heating to cooling or vice versa. | 47335 | h | s8 | 1 | 0 | 48 | 2 | R/W
Heat at room under temp. | This value indicates how many degrees under set room temp heating will be allowed | 47336 | °C | s8 | 10 | 5 | 100 | 10 | R/W
Cool at room over temp. | This value indicates how many degrees over set room temp cooling will be allowed | 47337 | °C | s8 | 10 | 5 | 100 | 10 | R/W
Cooling mix. valve amp. | Mixing valve amplification for the cooling valve | 47338 |  | s8 | 10 | 1 | 100 | 10 | R/W
Cooling mix. valve step delay |  | 47339 |  | s16 | 1 | 10 | 300 | 30 | R/W
Cooling with room sensor | Enables use of room sensor together with cooling 0=Off 1=On | 47340 |  | u8 | 10 | 0 | 1 | 0 | R/W
HPAC accessory | Activates the HPAC accessory | 47341 |  | u8 | 1 | 0 | 1 | 0 | R/W
HPAC DM start passive cooling | Value the degree minutes have to reach for the HPAC to start passive cooling | 47342 |  | s16 | 1 | 10 | 200 | 30 | R/W
HPAC DM start active cooling | Value the degree minutes have to reach for the HPAC to start active cooling | 47343 |  | s16 | 1 | 10 | 300 | 90 | R/W
SMS40 accessory | Activates the SMS40 accessory | 47352 |  | u8 | 1 | 0 | 1 | 0 | R/W
RMU System 1 | Activates the RMU accessory for system 1 | 47365 |  | u8 | 1 | 0 | 1 | 0 | R/W
RMU System 2 | Activates the RMU accessory for system 2 | 47366 |  | u8 | 1 | 0 | 1 | 0 | R/W
RMU System 3 | Activates the RMU accessory for system 3 | 47367 |  | u8 | 1 | 0 | 1 | 0 | R/W
RMU System 4 | Activates the RMU accessory for system 4 | 47368 |  | u8 | 1 | 0 | 1 | 0 | R/W
Allow Additive Heating | Whether to allow additive heating (only valid for operational mode Manual) | 47370 |  | u8 | 1 | 0 | 1 | 1 | R/W
Allow Heating | Whether to allow heating (only valid for operational mode Manual or Add. heat only) | 47371 |  | u8 | 1 | 0 | 1 | 1 | R/W
Allow Cooling | Whether to allow cooling (only valid for operational mode Manual or Add. heat only) | 47372 |  | u8 | 1 | 0 | 1 | 1 | R/W
Max diff. comp. |  | 47378 | °C | s16 | 10 | 10 | 250 | 100 | R/W
Max diff. add. |  | 47379 | °C | s16 | 10 | 10 | 240 | 70 | R/W
Low brine out autoreset | 0=Off 1=On | 47380 |  | u8 | 1 | 0 | 1 | 0 | R/W
Low brine out temp. |  | 47381 | °C | s16 | 10 | -120 | 150 | -80 | R/W
High brine in | Activates the High brine in temperature alarm. 0=Off 1=On | 47382 |  | u8 | 1 | 0 | 1 | 0 | R/W
High brine in temp. | The brine in temperature that triggers the high brine in temperature alarm (if active). | 47383 | °C | s16 | 10 | 100 | 300 | 200 | R/W
Date format | 1=DD-MM-YY 2=YY-MM-DD | 47384 |  | u8 | 1 | 1 | 2 | 1 | R/W
Time format | 12=12 hours 24=24 Hours | 47385 |  | u8 | 1 | 12 | 24 | 24 | R/W
HW production | Activates hot water production where applicable 0=Off 1=On | 47387 |  | u8 | 1 | 0 | 1 | 0 | R/W
Alarm lower room temp. | Lowers the room temperature during red light alarms to notify the occupants of the building that something is the matter 0=Off 1=On | 47388 |  | u8 | 1 | 0 | 1 | 0 | R/W
Alarm lower HW temp. | Lowers the hot water temperature during red light alarms to notify the occupants of the building that something is the matter 0=Off 1=On | 47389 |  | u8 | 1 | 0 | 1 | 1 | R/W
Use room sensor S4 | When activated the system uses the room sensor 0=Off 1=On | 47391 |  | u8 | 1 | 0 | 1 | 0 | R/W
Use room sensor S3 | When activated the system uses the room sensor 0=Off 1=On | 47392 |  | u8 | 1 | 0 | 1 | 0 | R/W
Use room sensor S2 | When activated the system uses the room sensor 0=Off 1=On | 47393 |  | u8 | 1 | 0 | 1 | 0 | R/W
Use room sensor S1 | When activated the system uses the room sensor 0=Off 1=On | 47394 |  | u8 | 1 | 0 | 1 | 0 | R/W
Room sensor setpoint S4 | Sets the room temperature setpoint for the system | 47395 | °C | s16 | 10 | 50 | 300 | 200 | R/W
Room sensor setpoint S3 | Sets the room temperature setpoint for the system | 47396 | °C | s16 | 10 | 50 | 300 | 200 | R/W
Room sensor setpoint S2 | Sets the room temperature setpoint for the system | 47397 | °C | s16 | 10 | 50 | 300 | 200 | R/W
Room sensor setpoint S1 | Sets the room temperature setpoint for the system | 47398 | °C | s16 | 10 | 50 | 300 | 200 | R/W
Room sensor factor S4 | Setting of how much the difference between set and actual room temperature should affect the supply temperature. | 47399 |  | u8 | 10 | 0 | 60 | 20 | R/W
Room sensor factor S3 | Setting of how much the difference between set and actual room temperature should affect the supply temperature. | 47400 |  | u8 | 10 | 0 | 60 | 20 | R/W
Room sensor factor S2 | Setting of how much the difference between set and actual room temperature should affect the supply temperature. | 47401 |  | u8 | 10 | 0 | 60 | 20 | R/W
Room sensor factor S1 | Setting of how much the difference between set and actual room temperature should affect the supply temperature. | 47402 |  | u8 | 10 | 0 | 60 | 20 | R/W
Speed circ.pump HW |  | 47413 | % | u8 | 1 | 0 | 100 | 70 | R/W
Speed circ.pump Heat |  | 47414 | % | u8 | 1 | 0 | 100 | 70 | R/W
Speed circ.pump Pool |  | 47415 | % | u8 | 1 | 0 | 100 | 70 | R/W
Speed circ.pump Economy |  | 47416 | % | u8 | 1 | 0 | 100 | 70 | R/W
Speed circ.pump Cooling |  | 47417 | % | u8 | 1 | 0 | 100 | 70 | R/W
Speed brine pump |  | 47418 | % | u8 | 1 | 0 | 100 | 75 | R/W
Night cooling | If the fan should have a higher speed when there is a high room temp and a low outdoor temp. 0=Off 1=On | 47537 |  | u8 | 1 | 0 | 1 | 0 | R/W
Start room temp. night cooling |  | 47538 | °C | u8 | 1 | 20 | 30 | 25 | R/W
Night Cooling Min. diff. | Minimum difference between room temp and outdoor temp to start night cooling | 47539 | °C | u8 | 1 | 3 | 10 | 6 | R/W
Heat DM diff | Difference in DM between compressor starts in heating mode | 47540 |  | s16 | 1 | 10 | 2000 | 60 | R/W
Cooling DM diff | Difference in DM between compressor starts in cooling mode | 47543 |  | s16 | 1 | 0 | 2000 | 30 | R/W
Operational mode | The operational mode of the heat pump 0=Auto 1=Manual 2=Add. heat only | 47570 |  | u8 | 1 | 0 | 0 | 0 | R/W
Max Internal Add | Maximum allowed steps for the internally connected addition. | 47613 |  | u8 | 1 | 0 | 7 | 3 | R/W
Int. connected add. mode | Binary or linear stepping method for the internally connected external addition. 0=Linear 1=Binary | 47614 |  | u8 | 1 | 0 | 1 | 0 | R/W
FLM 2 speed 4 |  | 48053 | % | u8 | 1 | 0 | 100 | 100 | R/W
FLM 2 speed 3 |  | 48054 | % | u8 | 1 | 0 | 100 | 80 | R/W
FLM 2 speed 2 |  | 48055 | % | u8 | 1 | 0 | 100 | 30 | R/W
FLM 2 speed 1 |  | 48056 | % | u8 | 1 | 0 | 100 | 0 | R/W
FLM 2 speed normal |  | 48057 | % | u8 | 1 | 0 | 100 | 65 | R/W
FLM 3 speed 4 |  | 48058 | % | u8 | 1 | 0 | 100 | 100 | R/W
FLM 3 speed 3 |  | 48059 | % | u8 | 1 | 0 | 100 | 80 | R/W
FLM 3 speed 2 |  | 48060 | % | u8 | 1 | 0 | 100 | 30 | R/W
FLM 3 speed 1 |  | 48061 | % | u8 | 1 | 0 | 100 | 0 | R/W
FLM 3 speed normal |  | 48062 | % | u8 | 1 | 0 | 100 | 65 | R/W
FLM 4 speed 4 |  | 48063 | % | u8 | 1 | 0 | 100 | 100 | R/W
FLM 4 speed 3 |  | 48064 | % | u8 | 1 | 0 | 100 | 80 | R/W
FLM 4 speed 2 |  | 48065 | % | u8 | 1 | 0 | 100 | 30 | R/W
FLM 4 speed 1 |  | 48066 | % | u8 | 1 | 0 | 100 | 0 | R/W
FLM 4 speed normal |  | 48067 | % | u8 | 1 | 0 | 100 | 65 | R/W
FLM 4 accessory | Activates the FLM 4 accessory | 48068 |  | u8 | 1 | 0 | 1 | 0 | R/W
FLM 3 accessory | Activates the FLM 3 accessory | 48069 |  | u8 | 1 | 0 | 1 | 0 | R/W
FLM 2 accessory | Activates the FLM 2 accessory | 48070 |  | u8 | 1 | 0 | 1 | 0 | R/W
FLM 1 accessory | Activates the FLM 1 accessory | 48071 |  | u8 | 1 | 0 | 1 | 0 | R/W
DM diff start add. | The value below the last compressor step the degree minutes needed to be reached for the pump to start electric addition | 48072 |  | s16 | 1 | 0 | 0 | 0 | R/W
FLM cooling | FLM cooling activated | 48073 |  | u8 | 1 | 0 | 1 | 0 | R/W
Set point for BT74 | Set point for change between cooling and heating when using BT74 | 48074 |  | s16 | 10 | 50 | 400 | 210 | R/W
Hot water tank type | 10=VPB 20=VPA | 48086 |  | u8 | 1 | 10 | 20 | 20 | R/W
Pool 2 accessory | Activate the pool 2 accessory | 48087 |  | u8 | 1 | 0 | 1 | 0 | R/W
Pool 1 accessory | Activates the pool 1 accessory | 48088 |  | u8 | 1 | 0 | 1 | 0 | R/W
Pool 2 start temp. | The Temperature below which the pool heating should start | 48089 | °C | s16 | 10 | 50 | 800 | 220 | R/W
Pool 1 start temp. | The Temperature below which the pool heating should start | 48090 | °C | s16 | 10 | 50 | 800 | 220 | R/W
Pool 2 stop temp. | The Temperature at which the pool heating will stop | 48091 | °C | s16 | 10 | 50 | 800 | 240 | R/W
Pool 1 stop temp. | The Temperature at which the pool heating will stop | 48092 | °C | s16 | 10 | 50 | 800 | 240 | R/W
Pool 2 Activated | Activates pool heating | 48093 |  | u8 | 1 | 0 | 1 | 1 | R/W
Pool 1 Activated | Activates pool heating | 48094 |  | u8 | 1 | 0 | 1 | 1 | R/W
HW Comfort | Activates the HW Comfort Accessory. | 48120 |  | u8 | 1 | 0 | 1 | 0 | R/W
Period Pool 2 |  | 48133 | min | u8 | 1 | 0 | 180 | 0 | R/W
DM startdiff add. with shunt |  | 48139 |  | s16 | 1 | 0 | 2000 | 400 | R/W
Max pool 2 compr. | Maximum number of compressors that are simultaneously charging the pool | 48140 |  | u8 | 1 | 1 | 18 | 18 | R/W
Max pool 1 compr. | Maximum number of compressors that are simultaneously charging the pool | 48141 |  | u8 | 1 | 1 | 18 | 18 | R/W
Step controlled add. start DM | DM diff from last compressor step where the first step of step controlled add. starts | 48142 |  | s16 | 1 | 0 | 2000 | 400 | R/W
HW Comfort add during Heat | Allows the HW Comfort addition to run during heating. | 48144 |  | u8 | 1 | 0 | 1 | 0 | R/W
HW Comfort mixing valve | Activates the HW Comfort Shunt. | 48145 |  | u8 | 1 | 0 | 1 | 0 | R/W
HW Comfort mixing valve amp. | Mixing valve amplification for the HW Comfort Accessory | 48146 |  | s8 | 10 | 1 | 100 | 10 | R/W
HW Comfort mixing valve wait | Wait time between changes of the mixing valve for the HW Comfort Accessory | 48147 | secs | s16 | 10 | 10 | 300 | 30 | R/W
HW Comfort hotwater temperature | The desired hotwater temperature | 48148 | °C | s8 | 10 | 40 | 65 | 55 | R/W
HW Comfort add. | Activates the HW Comfort Addition. | 48157 |  | u8 | 1 | 0 | 1 | 0 | R/W
Min cooling supply temp S4 | Minimum allowed supply temperature during cooling | 48174 | °C | s8 | 1 | 5 | 50 | 18 | R/W
Min cooling supply temp S3 | Minimum allowed supply temperature during cooling | 48175 | °C | s8 | 1 | 5 | 50 | 18 | R/W
Min cooling supply temp S2 | Minimum allowed supply temperature during cooling | 48176 | °C | s8 | 1 | 5 | 50 | 18 | R/W
Min cooling supply temp S1 | Minimum allowed supply temperature during cooling | 48177 | °C | s8 | 1 | 5 | 50 | 18 | R/W
Cooling supply temp. at 20°C | Supply Temperature at 20°C. Used to create cooling curve | 48178 | °C | s8 | 1 | 5 | 50 | 25 | R/W
Cooling supply temp. at 20°C | Supply Temperature at 20°C. Used to create cooling curve | 48179 | °C | s8 | 1 | 5 | 50 | 25 | R/W
Cooling supply temp. at 20°C | Supply Temperature at 20°C. Used to create cooling curve | 48180 | °C | s8 | 1 | 5 | 50 | 25 | R/W
Cooling supply temp. at 20°C | Supply Temperature at 20°C. Used to create cooling curve | 48181 | °C | s8 | 1 | 5 | 50 | 25 | R/W
Cooling supply temp. at 40°C | Supply Temperature at 40°C. Used to create cooling curve | 48182 | °C | s8 | 1 | 5 | 50 | 18 | R/W
Cooling supply temp. at 40°C | Supply Temperature at 40°C. Used to create cooling curve | 48183 | °C | s8 | 1 | 5 | 50 | 18 | R/W
Cooling supply temp. at 40°C | Supply Temperature at 40°C. Used to create cooling curve | 48184 | °C | s8 | 1 | 5 | 50 | 18 | R/W
Cooling supply temp. at 40°C | Supply Temperature at 40°C. Used to create cooling curve | 48185 | °C | s8 | 1 | 5 | 50 | 18 | R/W
Cooling use mix. valves | Close use valves during cooling mode | 48186 |  | u8 | 1 | 0 | 1 | 0 | R/W
Cooling use mix. valves | Close use valves during cooling mode | 48187 |  | u8 | 1 | 0 | 1 | 0 | R/W
Cooling use mix. valves | Close use valves during cooling mode | 48188 |  | u8 | 1 | 0 | 1 | 0 | R/W
Cooling use mix. valves | Close use valves during cooling mode | 48189 |  | u8 | 1 | 0 | 0 | 0 | R/W
Heatdump mix. valve delay | Mixing valve step delay for the heatdump valve | 48190 | s | s16 | 1 | 10 | 300 | 30 | R/W
Heatdump mix. valve amp. | Mixing valve amplification for the heatdump valve | 48191 |  | s8 | 10 | 1 | 100 | 10 | R/W
Cooldump mix. valve delay | Mixing valve step delay for the cooldump valve for the ACS-system | 48192 | s | s16 | 1 | 10 | 300 | 30 | R/W
Cooldump mix. valve amp. | Mixing valve amplification for the cooldump valve for the ACS-system | 48193 |  | s8 | 10 | 1 | 100 | 10 | R/W
ACS accessory | Activate the ACS accessory | 48194 |  | u8 | 1 | 0 | 1 | 0 | R/W
ACS heat dump 24h-function |  | 48195 |  | u8 | 1 | 0 | 1 | 0 | R/W
ACS run brinepump in wait mode |  | 48196 |  | u8 | 1 | 0 | 1 | 0 | R/W
ACS closingtime for cool dump |  | 48197 | s | u8 | 1 | 0 | 100 | 100 | R/W
ACS max cprs in active cooling |  | 48198 |  | u8 | 1 | 0 | 18 | 18 | R/W
ACS max brinepumps in passive cooling |  | 48199 |  | u8 | 1 | 0 | 18 | 18 | R/W